{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":18,"n_cols":10,"rows_kept":18,"merged":[[1,1,1,9],[3,2,3,9],[10,2,10,9],[13,2,13,7],[14,1,14,2],[15,2,15,9],[16,2,16,9],[17,1,17,9]],"flags":["formulas_cached_only"]}
[null,"附件1"]
[null,"广州市胸科医院负压机组及氧气室外管道改造需求明细"]
[null,"序号","项目","品牌规格","品牌","预计量","单位","单价","金额","备注"]
[null,"1","16号楼增加负压系统"]
[null,"1.1","医用真空负压机组","规格：2.2KW一用一备\n类别：撬装一体机\n(1)主泵体（油旋泵）：电机功率：2.2KW/台，最大抽速≥63m³/h，极限真空：0.1mbar，2台，1用1备\n(2)进气过滤器：真空泵口过滤装置2套\n(3）细菌过滤器：处理量≥63m³/h，过滤精度≥99.995%，2台\n(4)撬装及管路：型钢底座、烤漆工艺；机级内部304卫生级不锈钢管件及阀门；内置电缆/数据线，1套\n(5)中央控制系统：PLC控制，触摸屏，手动/自动切换，手自动双系统，系统自动轮询，断电自启，相序保护，含自动医用级报警系统，提供485远程信号；手机在线监控（机房须有4G信号）；远程运维平台，监测数据/曲线最长可保存30天，可导出/打印；环境温湿度监测；机头温度在线监测； 1套",null,1,"套"]
[null,"1.2","真空罐","标准立式真空罐，1.0立方米，-0.1MPa，材质:碳钢",null,1,"台"]
[null,"1.3","集污罐","50L，-0.1MPa，不锈钢，带观察窗",null,1,"台"]
[null,"1.4","机房管道","φ42*1.5，含紫铜接头和配件",null,30,"米"]
[null,"1.5","机房外管道","φ42*1.5，含紫铜接头和配件",null,40,"米"]
[null,"1.6","机组用电缆","阻燃铜芯交联聚乙烯绝缘聚氯乙烯护套电力电缆ZR-YJV-0.6/1KV-5*6mm2",null,15,"米"]
[null,"2","氧气室外管道改造"]
[null,"2.1","脱脂紫铜管","φ28*1.2，含紫铜接头和配件",null,75,"米"]
[null,"2.2","其他","墙面开孔、套管、焊接气体、焊条、支架、拉杆、螺丝、管卡、绝缘橡胶垫等",null,1,"批"]
[null,null,"总价（大写）：",{"$nulls":5},{"v":0,"d":"￥0.00"}]
[null,"说明："]
[null,null,"1、本报价为含运含税包安装报价。"]
[null,null,"2、设备货期为35天，改造项目工期为15天，质保期为1年"]
[null,"                                                                     公  司：\n                                                                     联系人：\n                                                                     电  话："]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}